## Slide 1: Chilled Surfaces: Ceilings, Floors, and Beams
Stanley A. Mumma, Ph.D., P.E. Prof. Emeritus, Architectural Engineering
PSU, Univ. Park, PA
sam11@psu.edu
Web: http://doas-radiant.psu.edu
ASHRAE Chapter, Meeting

## Slide 2: Key Learning Objectives
Chilled surface description and operating fundamentals
Current HVAC system of choice review
Conceptual integration of chilled surface systems into an HVAC system
A few of the 14 WIIFMe(s) of chilled surface systems
Applications
Perceived Cons of chilled surface systems
Conclusions

## Slide 3: Ceiling Radiant Panel

## Slide 4: Ceiling Radiant Panel

## Slide 5: Radiant Heating

## Slide 6: Radiant Cooling
Radiation 20 Btu/hr-ft2
Convection 14 Btu/hr-ft2
Total Sensible 34 Btu/hr-ft2
Ceiling ~60F

## Slide 7: Active Chilled Beam
I Beam
@ 45F?
No: It is the old
induction box system
applied by W H Carrier.

## Slide 8
Manufacturer A

## Slide 9
Manufacturer B

## Slide 10
Manufacturer C
EXHAUST AIR TO DOAS

## Slide 11
DOAS air
Induction Nozzle
Sen Cooling Coil
Room air
Manufacturer D
Beam Coil HT/ft 300-600 Btu/hr Vs. Ceiling panel HT/ft, 70 Btu/hr

## Slide 13
DOAS air
Induction Nozzle
Sen Cooling Coil
Room air

## Slide 14: Passive Chilled Beam

## Slide 15
Fluid in, 62-52F
75F, 40%
QTotal= up to 128-268 Btu/hr-linear ft cooling
32-46 fpm draft 3 ft below ceiling
Fluid out,66-56F

## Slide 16: Chilled Floor Best for atria areas or other with high solar loads on the floor.

## Slide 17: Chilled Floor

## Slide 19: Variable Air Volume (VAV) Current HVAC system of choice
AHU
1
2
3
4
Relief Air
OA,
Return Air
Sensible Cooling, ~20 Btu/hr-ft2
Many unsolved
inherant problems

## Slide 20: Inherent problems with VAV Systems
Poor air distribution.
Poor humidity control.
Poor acoustical properties.
Poor use of plenum and mechanical shaft space.
Serious control problems, particularly with tracking return fan systems.
Poor energy transport medium, air.
Poor resistance to the threat of biological and chemical terrorism, and
Poor and unpredictable ventilation performance.

## Slide 21: Chilled surface/Ventilation Air (DOAS) Arrangement
20-70% less OA than VAV
DOAS Unit W/ Energy Recovery
Cool/Dry Supply
Parallel Sen. Cooling System Chilled surfaces
High Induction Diffuser
Building With Sensible and Latent cooling decoupled
Pressurization

## Slide 22: WIIFMe: #1, K.I.S.S. But no simpler
Radiant is much
simpler than VAV

## Slide 23: WIIFMe: #2, First Cost Reduced?
Possible if system
designed properly!

## Slide 24: WIIFMe: #3, Energy demand (kW), & use (kWh) reduced
50% the kW
demand of VAV
58% the kWh
use of VAV

## Slide 25: WIIFMe: #5, 75% Smaller Mech. Rooms & Shafts

## Slide 26: WIIFMe: #8, Enhanced Env. Quality
Thermal Comfort
Velocity,
MRT, DBT,
RH, met, clo

## Slide 27: WIIFMe: #8, Enhanced Env. Quality
Thermal Comfort Testing
PMV: -0.01 to +0.07 PPD: 5.1 to 5.4% ASHRAE Std. PPD: 20%

## Slide 28: WIIFMe: #8, Enhanced Env. Quality
Proper heat balance on body

## Slide 29: WIIFMe: #9, Enhanced IAQ, Productivity, &
No recirculation: i.e.. 100% OA
Safety

## Slide 30: WIIFMe: #11, Reduced Plenum Depth
Duct
Suspended Ceiling

## Slide 31: WIIFMe: #12, A proven technology in the US
Pennsylvania Classroom

## Slide 32
Using radiant panels to temper cold OA

## Slide 33
DOAS Unit
Parallel sen. unit
Tempering OA without the loss of air side economizer!

## Slide 34
Midnight
Space T (MRT)
SA DBT
OA DBT
Panel Pump (P2) On
EW on/off
Free cooling performance data

## Slide 35: WIIFMe: #13, Applicable in many buildings, but not all
Excellent for:
commercial,
institutional,
educational,
medical.

## Slide 36: WIIFMe: #14, Applicable in virtually all climates

## Slide 37
Sooo.......... If it is so
great, When will the
LIGHTNING STRIKE?

## Slide 38
Perceived Con #1,
Condensation
Need never
occur! How?

## Slide 39
Condensation test, Open all doors and windows

## Slide 40
Back up condensate control

## Slide 41
Back up condensate control

## Slide 42: Perceived Con #2, Capacity
* 300 ft2/ton rule of thumb = 40 Btu/hr-ft2 * Radiant panel can remove about 35 Btu/hr-ft2, sen * Many conclude must cover the ceiling and part of the walls to provide the capacity. * But VAV can only provide up to 20 Btu/hr-ft2, sen * DOAS provides up to 6.5 Btu/hr-ft2, sen * Panel capacity req’d, 20-6.5=13.5 Btu/hr-ft2, sen * TRUTH: no capacity problem, and only need about 50% of the ceiling for spaces typical of office density. High density spaces will need less than 50%.

## Slide 43: Perceived Con #3, High 1st Cost
Case Study summary follows:

## Slide 44: 6 story 186,000 ft2 Office Building
Analysis uses VAV as a reference!
Chiller and pumps 1st cost reduced by 40%
Ductwork cost reduced by 75%
AHU’s reduced by 80%
Building Electrical service reduced
Building height per floor reduced
Lost rentable space devoted to mech. rooms and shafts recovered.
Savings: $1,405,000
Radiant panel add: $1,030,000
Net savings: $375,000 or $2/ft2

## Slide 45: For more information, see DOAS web page:
System related
  Chilled Ceilings in Parallel with Dedicated Outdoor Air Systems: Addressing the Concerns of Condensation, Capacity, and Cost http://doas-radiant.psu.edu/DOAS_RADIANT_HONOLULU_TP4573.pdf
Thermal Comfort
  Comfort With DOAS Radiant Cooling System http://doas-radiant.psu.edu/IAQ_comfort_04.pdf
Condensate control
  Chilled Ceiling Condensation Control http://doas-radiant.psu.edu/cond_control_fall_03.pdf
  Backup Condensation Control Via Portal Sensors http://doas-radiant.psu.edu/IAQ_winter_05.pdf

## Slide 46: For more information, see DOAS web page:
Fundamentals
  Ceiling Radiant Cooling Panels Employing Heat-Conducting Rails: Deriving the Governing Heat Transfer Equations http://doas-radiant.psu.edu/Xia_Mumma_CRCP_HCR_06.pdf
Design steps
  Designing a Dedicated Outdoor Air System with Ceiling Radiant Cooling Panels http://doas-radiant.psu.edu/Design_DOAS_CRCP_fall_06_Journal.pdf

## Slide 47: For more information, see DOAS web page:
Controls
  Direct Digital Temperature, Humidity, and Condensate Control for a Dedicated Outdoor Air-Ceiling Radiant Cooling Panel System
  http://doas-radiant.psu.edu/OR-05-3-3.pdf
Terror resistance
  DOAS and homeland security http://doas-radiant.psu.edu/ES_Jan_2007_DOAS_HS.pdf

## Slide 48: Conclusions
Chilled surface Technology Introduced.
A few WIIFMe Items Discussed
3 Perceived Cons dismissed
Chilled surface/DOAS Mech. Systems generate many LEED rating points
Natural environment and resources preserved; plus human health, Safety & productivity enhanced with Chilled Surface/DOAS !!
Helps assure a future for Our Children and Grand Children
I invite you to join with all of us who are implementing these exciting green technologies for the future!

## Slide 49
Questions