## Rechnung_mittel-Bezug_0100_GEA (hidden)
Zweileiter - Kühlen
[6 empty] | 1200 |  |  |  |  | 1500 |  |  |  |  | 1800
6er düse |  | m³/hm | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10
Model: Allometric1 |  | 10 | 13.5368 | 11.7516 | 9.5561 | 3.3333 | 12 | 16.2442 | 14.102 | 11.4673 | 4.1667 | 15 | 20.3052 | 17.6274 | 14.3341 | 5 | 18 | 24.3663 | 21.1529 | 17.201
|  | 15 | 17.5042 | 15.1958 | 12.3568 | 5 | 18 | 21.0051 | 18.235 | 14.8282 | 6.25 | 22.5 | 26.2563 | 22.7937 | 18.5352 | 7.5 | 27 | 31.5076 | 27.3525 | 22.2423
a | 3.1449 | 20 | 21.006 | 18.2358 | 14.8288 | 6.6667 | 24 | 25.2072 | 21.8829 | 17.7946 | 8.3333 | 30 | 31.509 | 27.3536 | 22.2432 | 10 | 36 | 37.8107 | 32.8244 | 26.6919
b | 0.63391 | 25 | 24.1978 | 21.0066 | 17.082 | 8.3333 | 30 | 29.0373 | 25.2079 | 20.4984 | 10.4167 | 37.5 | 36.2966 | 31.5099 | 25.623 | 12.5 | 45 | 43.556 | 37.8119 | 30.7476
|  | 30 | 27.1624 | 23.5803 | 19.1749 | 10 | 36 | 32.5949 | 28.2964 | 23.0098 | 12.5 | 45 | 40.7437 | 35.3705 | 28.7623 | 15 | 54 | 48.8924 | 42.4446 | 34.5148
|  | 35 | 29.9507 | 26.0009 | 21.1432 | 11.6667 | 42 | 35.9408 | 31.2011 | 25.3718 | 14.5833 | 52.5 | 44.9261 | 39.0013 | 31.7148 | 17.5 | 63 | 53.9113 | 46.8016 | 38.0578
8er düse |  | 40 | 32.5963 | 28.2976 | 23.0108 | 13.3333 | 48 | 39.1156 | 33.9571 | 27.613 | 16.6667 | 60 | 48.8945 | 42.4464 | 34.5163 | 20 | 72 | 58.6734 | 50.9357 | 41.4195
Model: Allometric1 |  | 45 | 35.1233 | 30.4913 | 24.7947 | 15 | 54 | 42.1479 | 36.5896 | 29.7536 | 18.75 | 67.5 | 52.6849 | 45.737 | 37.192 | 22.5 | 81 | 63.2219 | 54.8844 | 44.6304
|  | 50 | 37.5492 | 32.5973 | 26.5072 | 16.6667 | 60 | 45.0591 | 39.1168 | 31.8087 | 20.8333 | 75 | 56.3238 | 48.896 | 39.7609 | 25 | 90 | 67.5886 | 58.6752 | 47.713
a | 2.7302 | 55 | 39.8878 | 34.6275 | 28.1581 | 18.3333 | 66 | 47.8654 | 41.553 | 33.7898 | 22.9167 | 82.5 | 59.8317 | 51.9413 | 42.2372 | 27.5 | 99 | 71.7981 | 62.3295 | 50.6846
b | 0.63391 | 60 | 42.1497 | 36.5911 | 29.7549 | 20 | 72 | 50.5797 | 43.9094 | 35.7059 | 25 | 90 | 63.2246 | 54.8867 | 44.6323 | 30 | 108 | 75.8695 | 65.8641 | 53.5588
|  | 65 | 44.3436 | 38.4957 | 31.3036 | 21.6667 | 78 | 53.2123 | 46.1948 | 37.5643 | 27.0833 | 97.5 | 66.5154 | 57.7435 | 46.9554 | 32.5 | 117 | 79.8184 | 69.2922 | 56.3465
|  | 70 | 46.4764 | 40.3473 | 32.8093 | 23.3333 | 84 | 55.7717 | 48.4167 | 39.3711 | 29.1667 | 105 | 69.7147 | 60.5209 | 49.2139 | 35 | 126 | 83.6576 | 72.6251 | 59.0567
10er düse |  | 75 | 48.5542 | 42.151 | 34.276 | 25 | 90 | 58.2651 | 50.5812 | 41.1313 | 31.25 | 112.5 | 72.8313 | 63.2265 | 51.4141 | 37.5 | 135 | 87.3976 | 75.8719 | 61.6969
Model: Allometric1 |  | 80 | 50.5818 | 43.9113 | 35.7074 | 26.6667 | 96 | 60.6982 | 52.6935 | 42.8489 | 33.3333 | 120 | 75.8728 | 65.8669 | 53.5611 | 40 | 144 | 91.0473 | 79.0403 | 64.2733
|  | 85 | 52.5636 | 45.6316 | 37.1064 | 28.3333 | 102 | 63.0763 | 54.758 | 44.5277 | 35.4167 | 127.5 | 78.8453 | 68.4475 | 55.6596 | 42.5 | 153 | 94.6144 | 82.1369 | 66.7915
a | 2.2201 | 90 | 54.503 | 47.3153 | 38.4755 | 30 | 108 | 65.4036 | 56.7784 | 46.1706 | 37.5 | 135 | 81.7546 | 70.973 | 57.7133 | 45 | 162 | 98.1055 | 85.1676 | 69.2559
b | 0.63391 | 95 | 56.4034 | 48.9651 | 39.8171 | 31.6667 | 114 | 67.6841 | 58.7582 | 47.7805 | 39.5833 | 142.5 | 84.6052 | 73.4477 | 59.7256 | 47.5 | 171 | 101.5262 | 88.1372 | 71.6707
|  | 100 | 58.2676 | 50.5834 | 41.133 | 33.3333 | 120 | 69.9211 | 60.7001 | 49.3596 | 41.6667 | 150 | 87.4013 | 75.8751 | 61.6995 | 50 | 180 | 104.8816 | 91.0501 | 74.0394
|  | 105 | 60.0979 | 52.1723 | 42.4251 | 35 | 126 | 72.1174 | 62.6068 | 50.9101 | 43.75 | 157.5 | 90.1468 | 78.2585 | 63.6376 | 52.5 | 189 | 108.1761 | 93.9102 | 76.3651
|  | 110 | 61.8965 | 53.7338 | 43.6948 | 36.6667 | 132 | 74.2758 | 64.4805 | 52.4338 | 45.8333 | 165 | 92.8447 | 80.6007 | 65.5422 | 55 | 198 | 111.4137 | 96.7208 | 78.6507
|  | 115 | 63.6654 | 55.2694 | 44.9436 | 38.3333 | 138 | 76.3985 | 66.3233 | 53.9323 | 47.9167 | 172.5 | 95.4982 | 82.9042 | 67.4154 | 57.5 | 207 | 114.5978 | 99.485 | 80.8984
|  | 120 | 65.4065 | 56.7808 | 46.1726 | 40 | 144 | 78.4877 | 68.137 | 55.4071 | 50 | 180 | 98.1097 | 85.1713 | 69.2589 | 60 | 216 | 117.7316 | 102.2055 | 83.1107
|  | 125 | 67.1211 | 58.2694 | 47.383 | 41.6667 | 150 | 80.5453 | 69.9232 | 56.8596 | 52.0833 | 187.5 | 100.6817 | 87.4041 | 71.0745 | 62.5 | 225 | 120.818 | 104.8849 | 85.2894
|  | 130 | 68.8108 | 59.7362 | 48.5759 | 43.3333 | 156 | 82.573 | 71.6835 | 58.291 | 54.1667 | 195 | 103.2162 | 89.6044 | 72.8638 | 65 | 234 | 123.8595 | 107.5252 | 87.4365
|  | 135 | 70.4769 | 61.1826 | 49.752 | 45 | 162 | 84.5723 | 73.4191 | 59.7024 | 56.25 | 202.5 | 105.7153 | 91.7739 | 74.628 | 67.5 | 243 | 126.8584 | 110.1287 | 89.5536
|  | 140 | 72.1205 | 62.6095 | 50.9123 | 46.6667 | 168 | 86.5446 | 75.1314 | 61.0947 | 58.3333 | 210 | 108.1808 | 93.9142 | 76.3684 | 70 | 252 | 129.8169 | 112.6971 | 91.6421
|  | 145 | 73.7428 | 64.0178 | 52.0575 | 48.3333 | 174 | 88.4914 | 76.8214 | 62.469 | 60.4167 | 217.5 | 110.6142 | 96.0267 | 78.0863 | 72.5 | 261 | 132.737 | 115.2321 | 93.7035
|  | 150 | 75.3447 | 65.4085 | 53.1884 | 50 | 180 | 90.4137 | 78.4902 | 63.826 | 62.5 | 225 | 113.0171 | 98.1127 | 79.7825 | 75 | 270 | 135.6205 | 117.7353 | 95.739
|  | 155 | 76.9272 | 66.7823 | 54.3055 | 51.6667 | 186 | 92.3127 | 80.1387 | 65.1666 | 64.5833 | 232.5 | 115.3908 | 100.1734 | 81.4582 | 77.5 | 279 | 138.469 | 120.2081 | 97.7499
|  | 160 | 78.4911 | 68.1399 | 55.4095 | 53.3333 | 192 | 94.1893 | 81.7679 | 66.4914 | 66.6667 | 240 | 117.7367 | 102.2099 | 83.1143 | 80 | 288 | 141.284 | 122.6519 | 99.7371
|  | 165 | 80.0372 | 69.4822 | 56.501 | 55 | 198 | 96.0447 | 83.3786 | 67.8012 | 68.75 | 247.5 | 120.0559 | 104.2232 | 84.7514 | 82.5 | 297 | 144.067 | 125.0679 | 101.7017
|  | 170 | 81.5663 | 70.8096 | 57.5804 | 56.6667 | 204 | 97.8795 | 84.9715 | 69.0964 | 70.8333 | 255 | 122.3494 | 106.2144 | 86.3706 | 85 | 306 | 146.8193 | 127.4572 | 103.6447
|  | 175 | 83.079 | 72.1228 | 58.6482 | 58.3333 | 210 | 99.6948 | 86.5473 | 70.3779 | 72.9167 | 262.5 | 124.6185 | 108.1841 | 87.9723 | 87.5 | 315 | 149.5421 | 129.821 | 105.5668
|  | 180 | 84.5759 | 73.4223 | 59.705 | 60 | 216 | 101.4911 | 88.1067 | 71.6459 | 75 | 270 | 126.8639 | 110.1334 | 89.5574 | 90 | 324 | 152.2366 | 132.1601 | 107.4689
|  | 185 | 86.0577 | 74.7087 | 60.751 | 61.6667 | 222 | 103.2692 | 89.6504 | 72.9012 | 77.0833 | 277.5 | 129.0865 | 112.063 | 91.1265 | 92.5 | 333 | 154.9038 | 134.4756 | 109.3518
|  | 190 | 87.5249 | 75.9824 | 61.7867 | 63.3333 | 228 | 105.0299 | 91.1788 | 74.1441 | 79.1667 | 285 | 131.2873 | 113.9735 | 92.6801 | 95 | 342 | 157.5448 | 136.7683 | 111.2161
|  | 195 | 88.978 | 77.2439 | 62.8125 | 65 | 234 | 106.7736 | 92.6926 | 75.3751 | 81.25 | 292.5 | 133.467 | 115.8658 | 94.2188 | 97.5 | 351 | 160.1604 | 139.0389 | 113.0626
|  | 200 | 90.4176 | 78.4936 | 63.8288 | 66.6667 | 240 | 108.5011 | 94.1923 | 76.5945 | 83.3333 | 300 | 135.6263 | 117.7403 | 95.7432 | 100 | 360 | 162.7516 | 141.2884 | 114.8918
GEA-WT
[8 empty] | Approx. Über Origin / q/q110 mittel=f/Vwasser |  | 2000-01-13
[8 empty] | y0 |  | 0.46176
[8 empty] | A1 |  | 0.57752
[8 empty] | t1 |  | 51.9718
[8 empty] | A2 |  | 0.17134
[8 empty] | t2 |  | 581.433

## Sprache (hidden)
Ziel-Zelle | DE | GB | NL | Spanisch | Franz | Ital | Danish
B2 | Vierleiter | 2 water circuits | 4-pijps | 4 tubos | 4 tubes | 4 tubi | 4 rørs
D2 | Zweileiter | 1 water circuit | 2-pijps | 2 tubos | 2 tubes | 2 tubi | 2 rørs
A2 | Eingaben DID | Input DID | Gegevens DID | datos DID | données DID | dati DID | Input DID
B3 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
C3 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
D3 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
E3 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
A4 | Vwasser DID | Vwater DID | Waterhoeveelheid DID | V agua DID | V eau DID | Vacqua DID | V vand DID
A5 | Gerätelänge Ln | Unit length | Apparaatlengte | longitud | longueur nominale LN | Lunghezza nominale LN | Effektiv længde
A6 | Düsen Typ | Nozzle-type | Düsen Type | tipo de toberas | type de buse | Tipo di ugello | Dyse størrelse
A7 | Vluftprimär DID | Vair-primary DID | Primaire luchthoeveelheid | V aire primario | débit d'air primaire DID | Portata aria primaria DID | V primær luft
A9 | N-Düsen aktiv | No-nozzles active | Aantal düsen actief | n·toberas activas | buse N active | n° ugelli attivi | Antal aktive dyser
A10 | Eingabe Temperaturen | Input temperatures | Invoer temperaturen | datos temperatura | données températures | Temperature richieste | Temperatur set
A11 | Tluftprimär | Tair-primary | Temp. primairelucht | Temperatura aire primario | température d'air primaire | Temperatura aria primaria | T primær luft ind
A12 | Traum / rel. Luftfeuchte | Troom / rel. Humidity | Temp.ruimte | Temperatura ambiente | température ambiente | Temperatura ambiente | T rum
A13 | Twasser vor | Twater-flow | Temp.water intrede | Temperatura agua impulsion | température d'entrée d'eau | Temperatura acqua di entrata | T vand ind
A18 | Ergebnisse | results | Gegeven | resultados | résultats | risultati | Resultat
A20 | DTwasser | Dtwater | Temp. verschil water | Dt agua | DT température eau (entrée et sortie) | Dt acqua | DT vand
A21 | Twasser rück | Twater-return | Temp. retourwater | Temperatura agua retorno | température de l'eau de retour | Temperatura acqua di ritorno | T vand retur
A22 | DT Raum-vor | DT room - water flow | Temp. verschil ruimte-watertoev. | Dt ambiente agua | DT ambiente eau | Dt ambiente - acqua | DT rum ind
A23 | DT Raum-mittel | DT Room water average | Temp. verschil ruimte-gem.watertemp. | Dt amb.temp.media agua | DT ambiente eau moyenne | Dt ambiente - Tmedia dell'acqua | DT rum middel
A28 | Q wasser DID | Q water DID | Q water DID | Q agua DID | Q eau DID | Q acqua DID | Q vand DID
A29 | Q luft DID | Q air DID | Q lucht DID | Q aire DID | Q air DID | Q aria DID | Q luft DID
A30 | Q DID | Q DID | Q DID | Q DID | Q DID | Q totale DID | Q DID
A31 | DP wasser | DP water | DP water | Dp agua | DP eau | DP acqua | DP vand
A32 | DP luft | DP air | DP lucht | Dp aire | DP air | DP aria | DP luft
A33 | Lwa | NC (including 10 dB room absorbtion) | Lwa | Lwa | Lwa | Lwa | Lwa
A36 | vL | vL | vL | vL | vL | vL | vL
A37 | vH1 | vH1 | vH1 | vH1 | vH1 | vH1 | vH1
A38 | DTL | DTL | DTL | DTL | DTL | DTL | DTL
A39 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1
A40 | X-krit | X-krit | X-krit | X-krit | x-critique | x-critico | X-kritisk
A41 | Archimedes-Zahl | Archimedes-number | Archimedes-nummer | numero de Arquimedes | nombre d'Archimède | numero di Archimede | Archimedes-tal
A42 | DTzu | DTsupply | DT toevoer | DT impulsion | DT soufflage | Dt mandata | DT ind
F2 | Projekt | Project | Project | Proyecto | Projet | Progetto | Projekt
G2 | Raum-Nr. | room-No. | Ruimte-nr. | local No | numéro du local | Locale nr | Rum nr.
H2 | Bezeichnung | comment | Codering | referencia | désignation | Commento | Betegnelse
A1 | DID 300 Auslegung | DID 300 calculation | DID 300 selectie | calculo DID 300 | sélection DID 300 | Selezione DID 300 | DID 300 dimensionering
B10 | Kühlfall | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køle situation
D10 | Heizfall | heating | Verwarmen | calefacion | chauffage | riscaldamento | Varme situation
F10 | Eingaben Raumgeometrie | Input room measures | Opgave ruimteafmetingen | dimensiones local | dimensions du local | dimensioni del locale | Rum dimensioner
F11 | Raumhöhe | room height | Ruimtehoogte | altura | hauteur du local | altezza del locale | Rumhøjde
B18 | Vierleiter | 2 water circuits | 4-pijps | 4 tubos | 4 tubes | 4 tubi | 4 rørs
B19 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
C19 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
D18 | Zweileiter | 1 water circuit | 2-pijps | 2 tubos | 2 tubes | 2 tubi | 2 rørs
D19 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
E19 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
F36 | Hilfswerte | support values | Hulpwaarden | valores de ayuda | données complémentaires | dati complementari | Hjælpeværdier
F37 | N-Düsen nominell offen | N-active nozzles | N-Düsen standaard geopend | N-toberas activas | buse N active | n° ugelli attivi | N-dyser nominelt åbne
F38 | N-Düsen | N-nozzles total | N-Düsen | N-total de toberas | nombre de buses | numero totale ugelli | Dyse antal
F39 | Aeff | Aeff | Aeff | A efectiva | Aeff | Aeff | Aeff
F40 | veff | veff | veff | v efectiva | veff | veff | veff
F41 | H1 | H1 | H1 | H1 | H1 | H1 | H1
F42 | L | L | L | L | L | L | L
G30 | Sprache | Language | Taal | lenguaje | langue | lingua | Sprog
A14 | Twasser rück | Twater-return | Temp. retourwater | Temperatura agua retorno | température de l'eau de retour | T acqua di ritorno | T vand retur
| Einheit Primärluftvolumenstrom:l/s | Unit primary airflow:l/s | Hoeveelheid primaire lucht: l/s | aire primario en l/s | débit d'air primaire: l/s | portata aria primaria l/s | Enhed primærluft: l/s
| Einheit Primärluftvolumenstrom:m³/h | Unit primary airflow:m³/h | Hoeveelheid primaire lucht: m³/h | aire primario en m3/h | débit d'air primaire: m3/h | portata aria primaria m3/h | Enhed primærluft: m3/h
| Standard-Düsenanzahl(aktiv) wiederherstellen | Restore no. of standard active nozzles | Standaard aantal actieve düsen instellen | No.de tob.estand.activas | restauration nombre de buses actives standard | N° fuori standard di ugelli | Retur til standard dyseantal
| 70% - Gitter/Lochblech | 70% - free area | 70% - vrije doorlaat rooster | Reja chap.perforada 70% | 70%-grille/tôle perforée | Lamiera forata al 70% | 70% - frit areal
| 50% - Lochblech | 50% - free area | 50% - vrije doorlaat perforatie | chapa perforada 50% | 50%-tôle perforée | Lamiera forata al 50% | 50% - frit areal
| Details einblenden | details ON | details invoegen | details ON | détails on (afficher les détails) | Dettagli on (scoprire i dettagli) | detaljer on
| Details AUS | details OFF | details wissen | details OFF | détails off (ne plus afficher les détails) | Dettagli off (nascondere i dettagli) | detaljer off
| Vwasser DID = konst | Vwater DID = const | Vwater DID = const | Vwater DID = const | V eau DID=constant | Portata acqua DID=costante | V vand DID = konstant
| DTwasser DID = konst | DTwater DID = const | DTwater DID = const | DTwater DID = const | DT eau DID=constant | Dt acqua DID=costante | DT vand DID = konstant
| DID-Länge Ln ungültig | DID-lenght not valid | DID-lenght not valid | DID-lenght not valid | longueur DID Ln non valide | Lunghezza DID Ln non valida | Ugyldig længde
| Warnung: Gerätelänge | Attention: Unit length | Attention: Unit length | Attention: Unit length | attention: longueur de l'appareil | attenzione: lunghezza dell'apparechiatura | Bemærk: aggregatlængde
| Anzahl muss im Bereich von | No Nozzels must be | No Nozzels must be | No Nozzels must be | nombre des buses doit être compirs entre et | N° di ugelli deve essere compreso | Antal dyser skal være
| bis | to | to | to | à | fino a | til
| Warnung: Anzahl aktiver Düsen im nicht zulässigen Bereich | Attention: No of active nozzles not in allowed range | Attention: No of active nozzles not in allowed range | Attention: No of active nozzles not in allowed range | attention: nombre de buses actives non valid | Attenzione: numero di ugelli attivi non valido | Bemærk: Aktivt dyseantal ikke tilladt
| Düsenaustritts-Luftgeschwindigkeit zu gering | Nozzle-velocity too low | Nozzle-velocity too low | Nozzle-velocity too low | débit de sortie des buses trop faible | velocità uscita ugelli troppo bassa | Dysehastighed for lav
| muss größer als 7m/s sein | must be > 1375 fpm | must be > 7m/s | must be > 7m/s | doit être supérieur à 7m/s | deve essere > 7 m/s | Skal være > 7 m/s
| Warnung: Düsen-Luftaustrittsgeschwindigkeit | Attention: nozzle velocity | Attention: nozzle velocity | Attention: nozzle velocity | attention: débit de sortie des buses | Attenzione: velocità uscita ugelli | Bemærk: dysehastighed
| Wasservolumentrom zu hoch. | water-flow rate too high | water-flow rate too high | water-flow rate too high | débit d'eau trop élevé | portata acqua troppo elevata | Vand flow for højt
| Werte müssen unter 250 l/h liegen | must be below 1.5 GPM | must be below 250 l/h | must be below 250 l/h | valeurs doivent être inférieures à 250l/h | Valore deve essere inferiore a 250 l/h | skal være under 250 l/h
| Warnung: Wasservolumenstrom | Attention: water-flow rate | Attention: water-flow rate | Attention: water-flow rate | attention: débit d'eau | Attenzione al livello della portata dell'acqua | Bemærk: Tilladeligt vand flow
| Wasservolumentrom zu niedrig. | water-flow rate too low | water-flow rate too low | water-flow rate too low | débit d'eau trop faible | portata acqua troppo bassa | Vand flow for lavt
| Werte müssen über 30 l/h liegen | must be more than 0.132 GPM | must be more than 30 l/h | must be more than 30 l/h | valeurs doivent être supérieures à 30 l/h | Valore deve essere superiore a 30 l/h | skal være over 30 l/h
| Warnung: Wassertemp. Differenz | Attention: water temp.-difference | Attention: water temp.-difference | Attention: water temp.-difference | attention: différence de température d'eau | attenzione: Dt acqua | Bemærk: vand temp forskel
| Wassertemp.-Differenz unzulässig, | water temp.-difference not valid | water temp.-difference not valid | water temp.-difference not valid | différence de température d'eau non valide | Dt acqua non valido | vand temp forskel ikke tilladt
| muss zwischen 1K und 6K liegen | must be between 1.8 °F and 10.8 °F | must be between 1K and 6K | must be between 1K and 6K | doit être entre 1 K et 6K | deve essere compreso fra 1 K e 6 K | skal være mellem 1K og 6 K
| Wassertemp.-Differenz unzulässig, | Attention: water temp.-difference, | Attention: water temp.-difference, | Attention: water temp.-difference, | différence de température d'eau non valide | Attenzione: Dt acqua | Bemærk: vand temp forskel
| muss zwischen 5K und 30K liegen | must be between 9 °F and 54 °F | must be between 5K and 30K | must be between 5K and 30K | doit être entre 5K et 20K | deve essere compreso fra 5 K e 30 K | skal være mellem 5K og 30K
F30 | Layout Frontteil | layout room-face | layout rooster | layout perforada | layout perforée | disegno ambiente | Perforering på frontplade
F28 | Achtung : Taupunktunterschreitung | Attention : passing below the dew point | Attention : passing below the dew point | Attention : passing below the dew point | Attention : passing below the dew point | Attenzione: condizioni al di sotto del punto di rugiada | Attention : passing below the dew point
F43 | Taupunkttemperatur-Kühlfall | room air dew point-cooling | room air dew point-cooling | room air dew point-cooling | room air dew point-cooling | punto di rugiada aria/ambiente | room air dew point-cooling
A43 | Stutzen-Durchmesser / Primärluft | Connection-diameter / primary air | Connection-diameter / primary air | Connection-diameter / primary air | Connection-diameter / primary air | Diametro connessione / aria primaria | Connection-diameter / primary air
| muss zwischen 900 und 3000mm liegen | must be 3 to 10 ft | must be 900 to 3000mm | must be 900 to 3000mm | doit être compris entre 900 et 3000 mm | deve essere compreso fra 900 e 3000 | Skal være 900 - 3000 mm

## DP_Wasser_GEA (hidden)
| Vierleiter-Kühlen |  | Vierleiter-heizen |  | Zweileiter - Kühlen |  | Zweileiter- Heizen
| Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT
Rohrlänge | 1.71 |  | 1.71 |  | 1.71 |  | 1.71
Anzahl Rohre : | 6 |  | 2 |  | 8 |  | 8
Anzahl Rohrbögen(90°) : | 10 | 2 | 2 | 2 | 14 | 2 | 14 | 2
z-Wert pro Bogen: | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Rohrlänge pro Wasserkreis: | 10.26 | 0.4 | 3.42 | 0.4 | 13.68 | 0.4 | 13.68 | 0.4
sonstige z-Werte : |  | 1.5 |  | 1.5 |  | 1.5 |  | 1.5
z-Wert pro Wasserkreis: | 7 | 2.9 | 1.4 | 2.9 | 9.8 | 2.9 | 9.8 | 2.9
Di -Rohr: | 0.0113 | 0.011 | 0.0113 | 0.011 | 0.0113 | 0.011 | 0.0113 | 0.011
Wassertemp. | 58.4854 | 58.4854 | 169.4978 | 169.4978 | 58.6354 | 58.6354 | 170.1876 | 170.1876

## Katalog_DID300
DID 300 calculation | [10 empty] | Vierleiter-Kühlen | Vierleiter-heizen | Zweileiter-kühlen | Zweileiter-heizen
Input DID | 2 water circuits |  | 1 water circuit |  | Project | room-No. | comment |  |  | 6er düse | 2.7313 | 1.8209 | 3.0348 | 3.0348 | Faktor Vierleiter Kühlen | 0.9
| cooling | heating | cooling | heating | [5 empty] | Model: Allometric1 | 0.63391 | 0.63391 | 0.63391 | 0.63391 | Faktor Vierleiter Heizen | 0.6
Vwater DID | 1.5 | 0.8 | 1.5 | 1.5 | [5 empty] | 8er düse | 2.3711 | 1.5808 | 2.6346 | 2.6346
Unit length | 6 | [8 empty] | Model: Allometric1 | 0.63391 | 0.63391 | 0.63391 | 0.63391 | Faktor / WT-Abstand | 0.965
Nozzle-type | b | [8 empty] | 10er düse | 1.9281 | 1.2854 | 2.1424 | 2.1424
Vair-primary DID | 75 | [8 empty] | Model: Allometric1 | 0.63391 | 0.63391 | 0.63391 | 0.63391
35.4167
No-nozzles active | 64
Input temperatures | cooling |  | heating |  | Input room measures
Tair-primary | 55 |  | 55 |  | room height | 10 |  | Parameter | Aktiv | gesamt
Troom / rel. Humidity | 75 | 50 | 72 | 50 | A | 10 |  | ------------------------------------------------------------
Twater-flow | 57 |  | 180 |  | X | 4 |  | A | -188.5 | -209.3333
Twater-return | 64.6 |  | 116 |  |  |  |  | B1 | 0.60635 | 0.65723
[8 empty] | B2 | -0.00064289 | -0.00067593
[8 empty] | B3 | 3.3779e-07 | 3.4549e-07
[8 empty] | B4 | -8.4643e-11 | -8.4175e-11
results | 2 water circuits |  | 1 water circuit |  |  |  |  | B5 | 8.1777e-15 | 7.9139e-15
| cooling | heating | cooling | heating
Dtwater | -2.9707 | 21.0044 | -3.2708 | 19.6249
Twater-return | 59.9707 | 158.9956 | 60.2708 | 160.3751 |  |  |  | Parameter | aktiv | Gesamt
DT room - water flow | -18 | 108 | -18 | 108 |  |  |  | ------------------------------------------------------------
DT Room water average | -16.5146 | 97.4978 | -16.3646 | 98.1876 |  |  |  | A | -116.0151 | -144.5148
DT-Raum -vor soll | -18 | 108 | -18 | 108 |  |  |  | B1 | 0.38485 | 0.45915
| 0 | 0 | 0 | 0 |  |  |  | B2 | -0.00038796 | -0.00044796
| 1.609 | 0.85815 | 1.609 | 1.609 |  |  |  | B3 | 1.9919e-07 | 2.2155e-07
| 0.10903 | 0.058148 | 0.10903 | 0.10903 |  |  |  | B4 | -4.8754e-11 | -5.2082e-11
Q water DID | -2231.2272 | 8413.7672 | -2456.6168 | 14739.7008 | Attention : passing below the dew point |  |  | B5 | 4.6088e-15 | 4.7225e-15
Q air DID | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Q DID | #VALUE! | #VALUE! | #VALUE! | #VALUE! | layout room-face | Language
DP water | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DP air | 0.43747
NC (including 10 dB room absorbtion) | 24.9336
Stand : 07.03.2005
vL | 90.2091 |  | 90.2091 |  | support values
vH1 | 48.7375 |  | 48.7375 |  | N-active nozzles | 56
DTL | -2.0628 |  | -2.0492 |  | N-nozzles total | 64
DTH1 | -0.48755 |  | -0.26908 |  | Aeff | 0.034627
X-krit | 9.8576 |  | 10.0002 |  | veff | 2165.9148
Archimedes-number | 0.00014917 |  | 0.00014455 |  | H1 | 4.42
DTsupply | 17.3445 |  | 17.2302 |  | L | 8.42
Connection-diameter / primary air | 3.8583 |  |  |  | room air dew point-cooling | #VALUE!
Re wasser | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.96715
F wasser | 1.1144 | 1.0677 | 1.1144 | 1.1144 |  |  | 0
| 12.0219 | 24.8793 | 43.2788 | 43.2788
69.7178
Taupkt °C | #VALUE! | #VALUE!
X g/kg | #VALUE! | #VALUE!
Note on A5: effective lenght Ln
Note on A6: A, B or C
Note on A28: sensible heat
Note on A29: primary air
Note on B4: Flow-rates above 1.5 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on C4: Flow-rates above 1.5 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on D4: Flow-rates above 1.5 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on E4: Flow-rates above 1.5 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on G12: if value is red: check X-krit