## Rechnung_mittel-Bezug_0100_GEA (hidden)
Werte für Origin - GEA einreihig - Zweileiter | [6 empty] | Werte für Origin - GEA zweireihig - Vierleiter-kühlen | [6 empty] | Werte für Origin - GEA zweireihig - Vierleiter heizen
6 |  | 8 |  | 10 |  |  | 6 |  | 8 |  | 10 |  |  | 6 |  | 8 |  | 10
m³/mh | W/Km - mittel | m³/mh | W/Km - mittel | m³/mh | W/Km - mittel |  | m³/mh | W/Km - mittel | m³/mh | W/Km - mittel | m³/mh | W/Km - mittel |  | m³/mh | W/Km - mittel | m³/mh | W/Km - mittel | m³/mh | W/Km - mittel
43.8784 | 44.9006 | 98.9505 | 58.7228 | 120.4609 | 56.464 |  | 42.4685 | 48.1506 | 127.8199 | 88.901 | 58.6071 | 38.3396 |  | 41.6191 | 28.1766 | 60.0303 | 30.543 | 64.1745 | 25.6141
60.7412 | 54.1201 | 73.2642 | 50.4946 | 81.7312 | 46.3151 |  | 64.4878 | 66.7323 | 100.4714 | 76.4839 | 85.0504 | 51.9978 |  | 62.8979 | 36.912 | 60.1163 | 30.5818 | 85.3286 | 31.8123
83.7677 | 64.4684 | 52.9039 | 40.7245 | 59.5812 | 38.0263 |  | 84.5303 | 80.8228 | 79.8436 | 66.0634 | 122.6307 | 68.7642 |  | 82.8329 | 43.7079 | 88.1355 | 39.1021 | 120.1732 | 39.0448
82.8039 | 63.9365 | 39.9434 | 33.4241 | 60.0427 | 38.2763 |  | 83.3958 | 78.0271 | 62.8022 | 55.7742 | 86.7607 | 53.4968 |  |  |  | 116.3702 | 45.9402
36.6312 | 40.7431 | [5 empty] | 62.5719 | 64.2173 | 106.6347 | 79.2119 | 128.5532 | 69.3308 |  |  |  | 44.2271 | 24.7415
[7 empty] | 35.6823 | 40.3244 | 58.8366 | 51.2383 | 88.0399 | 53.2744
[9 empty] | 80.5801 | 64.9722 | 63.6881 | 40.5954
[9 empty] | 42.7316 | 37.893
Parameter | Value | Parameter | Value | Parameter | Value |  | Parameter | Value | Parameter | Value | Parameter | Value |  | Parameter | Value | Parameter | Value | Parameter | Value
a | 5.1844 | a | 4.2697 | a | 3.7094 |  | a | 2.9985 | a | 2.5089 | a | 1.9304 |  | a | 2.5946 | a | 2.2075 | a | 1.8221
b | 0.57 | b | 0.57 | b | 0.57 |  | b | 0.74 | b | 0.74 | b | 0.74 |  | b | 0.64 | b | 0.64 | b | 0.64
|  | mm² | %
| 6 | 28.2743 | -43.75%
| 8 | 50.2655 | 0%
| 10 | 78.5398 | 56.25%
Zweileiter - Kühlen | [21 empty] | Vierleiter - Kühlen | [21 empty] | Vierleiter - heizen
[7 empty] | 900 |  |  |  |  | 1200 |  |  |  |  | 1500 | [11 empty] | 900 |  |  |  |  | 1200 |  |  |  |  | 1500 | [10 empty] | 900 |  |  |  |  | 1200 |  |  |  |  | 1500
6er düse |  |  | m³/hm | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | 6er düse |  |  | m³/hm | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | 6er düse |  | m³/hm | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10 | l/s | m³/h | 6 | 8 | 10
Model: Allometric1 |  |  | 10 | 19.2617 | 15.8636 | 13.7819 | 2.5 | 9 | 17.3356 | 14.2772 | 12.4037 | 3.3333 | 12 | 23.1141 | 19.0363 | 16.5383 | 4.1667 | 15 | 28.8926 | 23.7953 | 20.6728 | Model: Allometric1 |  |  | 10 | 16.4778 | 13.7874 | 10.6082 | 2.5 | 9 | 14.83 | 12.4086 | 9.5474 | 3.3333 | 12 | 19.7734 | 16.5449 | 12.7298 | 4.1667 | 15 | 24.7167 | 20.6811 | 15.9123 | Model: Allometric1 |  | 10 | 11.326 | 9.6362 | 7.9536 | 2.5 | 9 | 10.1934 | 8.6726 | 7.1583 | 3.3333 | 12 | 13.5912 | 11.5635 | 9.5443 | 4.1667 | 15 | 16.989 | 14.4543 | 11.9304
|  |  | 15 | 24.2699 | 19.9881 | 17.3652 | 3.75 | 13.5 | 21.8429 | 17.9893 | 15.6287 | 5 | 18 | 29.1238 | 23.9858 | 20.8383 | 6.25 | 22.5 | 36.4048 | 29.9822 | 26.0478 |  |  |  | 15 | 22.2437 | 18.6118 | 14.3202 | 3.75 | 13.5 | 20.0193 | 16.7506 | 12.8882 | 5 | 18 | 26.6925 | 22.3342 | 17.1842 | 6.25 | 22.5 | 33.3656 | 27.9177 | 21.4803 |  |  | 15 | 14.6816 | 12.4912 | 10.3101 | 3.75 | 13.5 | 13.2135 | 11.2421 | 9.2791 | 5 | 18 | 17.6179 | 14.9895 | 12.3721 | 6.25 | 22.5 | 22.0224 | 18.7368 | 15.4652
a | 5.1844 |  | 20 | 28.5945 | 23.5498 | 20.4595 | 5 | 18 | 25.735 | 21.1948 | 18.4136 | 6.6667 | 24 | 34.3134 | 28.2598 | 24.5514 | 8.3333 | 30 | 42.8917 | 35.3247 | 30.6893 | a | 2.9985 |  | 20 | 27.5209 | 23.0273 | 17.7175 | 5 | 18 | 24.7688 | 20.7246 | 15.9458 | 6.6667 | 24 | 33.025 | 27.6328 | 21.261 | 8.3333 | 30 | 41.2813 | 34.541 | 26.5763 | a | 2.5946 | 20 | 17.6496 | 15.0164 | 12.3944 | 5 | 18 | 15.8846 | 13.5148 | 11.1549 | 6.6667 | 24 | 21.1795 | 18.0197 | 14.8732 | 8.3333 | 30 | 26.4744 | 22.5246 | 18.5915
b | 0.57 |  | 25 | 32.4729 | 26.744 | 23.2345 | 6.25 | 22.5 | 29.2256 | 24.0696 | 20.9111 | 8.3333 | 30 | 38.9675 | 32.0928 | 27.8815 | 10.4167 | 37.5 | 48.7093 | 40.116 | 34.8518 | b | 0.74 |  | 25 | 32.462 | 27.1617 | 20.8986 | 6.25 | 22.5 | 29.2158 | 24.4455 | 18.8087 | 8.3333 | 30 | 38.9544 | 32.5941 | 25.0783 | 10.4167 | 37.5 | 48.693 | 40.7426 | 31.3478 | b | 0.64 | 25 | 20.359 | 17.3216 | 14.2971 | 6.25 | 22.5 | 18.3231 | 15.5894 | 12.8674 | 8.3333 | 30 | 24.4308 | 20.7859 | 17.1565 | 10.4167 | 37.5 | 30.5385 | 25.9824 | 21.4456
|  |  | 30 | 36.0292 | 29.6729 | 25.7791 | 7.5 | 27 | 32.4263 | 26.7056 | 23.2012 | 10 | 36 | 43.235 | 35.6074 | 30.9349 | 12.5 | 45 | 54.0438 | 44.5093 | 38.6686 |  |  |  | 30 | 37.1509 | 31.085 | 23.9172 | 7.5 | 27 | 33.4358 | 27.9765 | 21.5255 | 10 | 36 | 44.5811 | 37.302 | 28.7006 | 12.5 | 45 | 55.7264 | 46.6276 | 35.8758 |  |  | 30 | 22.8788 | 19.4654 | 16.0666 | 7.5 | 27 | 20.5909 | 17.5189 | 14.4599 | 10 | 36 | 27.4545 | 23.3585 | 19.2799 | 12.5 | 45 | 34.3182 | 29.1982 | 24.0998
|  |  | 35 | 39.3382 | 32.3981 | 28.1467 | 8.75 | 31.5 | 35.4043 | 29.1583 | 25.332 | 11.6667 | 42 | 47.2058 | 38.8777 | 33.776 | 14.5833 | 52.5 | 59.0072 | 48.5971 | 42.22 |  |  |  | 35 | 41.6399 | 34.8411 | 26.8072 | 8.75 | 31.5 | 37.4759 | 31.357 | 24.1264 | 11.6667 | 42 | 49.9679 | 41.8093 | 32.1686 | 14.5833 | 52.5 | 62.4599 | 52.2617 | 40.2107 |  |  | 35 | 25.251 | 21.4838 | 17.7324 | 8.75 | 31.5 | 22.7259 | 19.3354 | 15.9592 | 11.6667 | 42 | 30.3012 | 25.7805 | 21.2789 | 14.5833 | 52.5 | 37.8765 | 32.2256 | 26.5987
8er düse |  |  | 40 | 42.4492 | 34.9603 | 30.3726 | 10 | 36 | 38.2043 | 31.4642 | 27.3354 | 13.3333 | 48 | 50.939 | 41.9523 | 36.4472 | 16.6667 | 60 | 63.6738 | 52.4404 | 45.559 | 8er düse |  |  | 40 | 45.9647 | 38.4597 | 29.5914 | 10 | 36 | 41.3682 | 34.6137 | 26.6322 | 13.3333 | 48 | 55.1576 | 46.1517 | 35.5096 | 16.6667 | 60 | 68.947 | 57.6896 | 44.387 | 8er düse |  | 40 | 27.5039 | 23.4005 | 19.3145 | 10 | 36 | 24.7535 | 21.0604 | 17.383 | 13.3333 | 48 | 33.0046 | 28.0806 | 23.1774 | 16.6667 | 60 | 41.2558 | 35.1007 | 28.9717
Model: Allometric1 |  |  | 45 | 45.3969 | 37.3879 | 32.4818 | 11.25 | 40.5 | 40.8572 | 33.6491 | 29.2336 | 15 | 54 | 54.4763 | 44.8655 | 38.9781 | 18.75 | 67.5 | 68.0954 | 56.0819 | 48.7226 | Model: Allometric1 |  |  | 45 | 50.1507 | 41.9623 | 32.2863 | 11.25 | 40.5 | 45.1356 | 37.766 | 29.0576 | 15 | 54 | 60.1808 | 50.3547 | 38.7435 | 18.75 | 67.5 | 75.226 | 62.9434 | 48.4294 | Model: Allometric1 |  | 45 | 29.6573 | 25.2326 | 20.8267 | 11.25 | 40.5 | 26.6916 | 22.7094 | 18.7441 | 15 | 54 | 35.5887 | 30.2792 | 24.9921 | 18.75 | 67.5 | 44.4859 | 37.849 | 31.2401
|  |  | 50 | 48.2068 | 39.7021 | 34.4922 | 12.5 | 45 | 43.3861 | 35.7319 | 31.043 | 16.6667 | 60 | 57.8481 | 47.6425 | 41.3907 | 20.8333 | 75 | 72.3102 | 59.5531 | 51.7383 |  |  |  | 50 | 54.2173 | 45.3648 | 34.9043 | 12.5 | 45 | 48.7955 | 40.8284 | 31.4138 | 16.6667 | 60 | 65.0607 | 54.4378 | 41.8851 | 20.8333 | 75 | 81.3259 | 68.0473 | 52.3564 |  |  | 50 | 31.7261 | 26.9928 | 22.2795 | 12.5 | 45 | 28.5535 | 24.2935 | 20.0516 | 16.6667 | 60 | 38.0713 | 32.3913 | 26.7354 | 20.8333 | 75 | 47.5891 | 40.4892 | 33.4193
a | 4.2697 |  | 55 | 50.8981 | 41.9186 | 36.4179 | 13.75 | 49.5 | 45.8083 | 37.7268 | 32.7761 | 18.3333 | 66 | 61.0778 | 50.3024 | 43.7015 | 22.9167 | 82.5 | 76.3472 | 62.878 | 54.6269 | a | 2.5089 |  | 55 | 58.1792 | 48.6799 | 37.4549 | 13.75 | 49.5 | 52.3613 | 43.8119 | 33.7094 | 18.3333 | 66 | 69.8151 | 58.4159 | 44.9459 | 22.9167 | 82.5 | 87.2689 | 73.0199 | 56.1824 | a | 2.2075 | 55 | 33.7216 | 28.6905 | 23.6808 | 13.75 | 49.5 | 30.3494 | 25.8215 | 21.3128 | 18.3333 | 66 | 40.4659 | 34.4286 | 28.417 | 22.9167 | 82.5 | 50.5823 | 43.0358 | 35.5213
b | 0.57 |  | 60 | 53.4862 | 44.0501 | 38.2697 | 15 | 54 | 48.1375 | 39.6451 | 34.4427 | 20 | 72 | 64.1834 | 52.8601 | 45.9236 | 25 | 90 | 80.2292 | 66.0751 | 57.4045 | b | 0.74 |  | 60 | 62.0485 | 51.9175 | 39.9459 | 15 | 54 | 55.8437 | 46.7257 | 35.9513 | 20 | 72 | 74.4583 | 62.301 | 47.9351 | 25 | 90 | 93.0728 | 77.8762 | 59.9189 | b | 0.64 | 60 | 35.6527 | 30.3336 | 25.037 | 15 | 54 | 32.0874 | 27.3002 | 22.5333 | 20 | 72 | 42.7832 | 36.4003 | 30.0444 | 25 | 90 | 53.479 | 45.5003 | 37.5555
|  |  | 65 | 55.9829 | 46.1064 | 40.0561 | 16.25 | 58.5 | 50.3847 | 41.4957 | 36.0505 | 21.6667 | 78 | 67.1795 | 55.3277 | 48.0674 | 27.0833 | 97.5 | 83.9744 | 69.1596 | 60.0842 |  |  |  | 65 | 65.8348 | 55.0855 | 42.3835 | 16.25 | 58.5 | 59.2513 | 49.577 | 38.1451 | 21.6667 | 78 | 79.0018 | 66.1026 | 50.8602 | 27.0833 | 97.5 | 98.7522 | 82.6283 | 63.5752 |  |  | 65 | 37.5267 | 31.928 | 26.353 | 16.25 | 58.5 | 33.774 | 28.7352 | 23.7177 | 21.6667 | 78 | 45.032 | 38.3136 | 31.6236 | 27.0833 | 97.5 | 56.29 | 47.8919 | 39.5295
|  |  | 70 | 58.3984 | 48.0957 | 41.7844 | 17.5 | 63 | 52.5586 | 43.2861 | 37.606 | 23.3333 | 84 | 70.0781 | 57.7148 | 50.1413 | 29.1667 | 105 | 87.5976 | 72.1436 | 62.6766 |  |  |  | 70 | 69.546 | 58.1908 | 44.7727 | 17.5 | 63 | 62.5914 | 52.3717 | 40.2954 | 23.3333 | 84 | 83.4552 | 69.8289 | 53.7272 | 29.1667 | 105 | 104.319 | 87.2862 | 67.159 |  |  | 70 | 39.3494 | 33.4788 | 27.633 | 17.5 | 63 | 35.4145 | 30.1309 | 24.8697 | 23.3333 | 84 | 47.2193 | 40.1745 | 33.1596 | 29.1667 | 105 | 59.0241 | 50.2181 | 41.4495
10er düse |  |  | 75 | 60.7407 | 50.0248 | 43.4604 | 18.75 | 67.5 | 54.6667 | 45.0223 | 39.1143 | 25 | 90 | 72.8889 | 60.0298 | 52.1524 | 31.25 | 112.5 | 91.1111 | 75.0372 | 65.1905 | 10er düse |  |  | 75 | 73.1889 | 61.2388 | 47.1179 | 18.75 | 67.5 | 65.87 | 55.115 | 42.4061 | 25 | 90 | 87.8266 | 73.4866 | 56.5415 | 31.25 | 112.5 | 109.7833 | 91.8583 | 70.6768 | 10er düse |  | 75 | 41.1258 | 34.9902 | 28.8805 | 18.75 | 67.5 | 37.0132 | 31.4911 | 25.9924 | 25 | 90 | 49.351 | 41.9882 | 34.6566 | 31.25 | 112.5 | 61.6887 | 52.4852 | 43.3207
Model: Allometric1 |  |  | 80 | 63.0168 | 51.8993 | 45.0889 | 20 | 72 | 56.7151 | 46.7094 | 40.58 | 26.6667 | 96 | 75.6202 | 62.2792 | 54.1067 | 33.3333 | 120 | 94.5252 | 77.849 | 67.6334 | Model: Allometric1 |  |  | 80 | 76.7691 | 64.2345 | 49.4228 | 20 | 72 | 69.0922 | 57.811 | 44.4805 | 26.6667 | 96 | 92.1229 | 77.0814 | 59.3073 | 33.3333 | 120 | 115.1536 | 96.3517 | 74.1342 | Model: Allometric1 |  | 80 | 42.8601 | 36.4657 | 30.0983 | 20 | 72 | 38.5741 | 32.8191 | 27.0885 | 26.6667 | 96 | 51.4321 | 43.7588 | 36.118 | 33.3333 | 120 | 64.2901 | 54.6985 | 45.1475
|  |  | 85 | 65.2325 | 53.7241 | 46.6742 | 21.25 | 76.5 | 58.7092 | 48.3517 | 42.0068 | 28.3333 | 102 | 78.279 | 64.4689 | 56.0091 | 35.4167 | 127.5 | 97.8487 | 80.5862 | 70.0113 |  |  |  | 85 | 80.2915 | 67.1818 | 51.6905 | 21.25 | 76.5 | 72.2624 | 60.4636 | 46.5214 | 28.3333 | 102 | 96.3498 | 80.6182 | 62.0286 | 35.4167 | 127.5 | 120.4373 | 100.7727 | 77.5357 |  |  | 85 | 44.5557 | 37.9083 | 31.2891 | 21.25 | 76.5 | 40.1002 | 34.1175 | 28.1602 | 28.3333 | 102 | 53.4669 | 45.49 | 37.5469 | 35.4167 | 127.5 | 66.8336 | 56.8625 | 46.9337
a | 3.7094 |  | 90 | 67.3928 | 55.5033 | 48.2199 | 22.5 | 81 | 60.6535 | 49.953 | 43.3979 | 30 | 108 | 80.8713 | 66.6039 | 57.8639 | 37.5 | 135 | 101.0892 | 83.2549 | 72.3299 | a | 1.9304 |  | 90 | 83.7605 | 70.0844 | 53.9237 | 22.5 | 81 | 75.3844 | 63.0759 | 48.5314 | 30 | 108 | 100.5126 | 84.1012 | 64.7085 | 37.5 | 135 | 125.6407 | 105.1265 | 80.8856 | a | 1.8221 | 90 | 46.2158 | 39.3208 | 32.4549 | 22.5 | 81 | 41.5942 | 35.3887 | 29.2094 | 30 | 108 | 55.459 | 47.1849 | 38.9459 | 37.5 | 135 | 69.3237 | 58.9811 | 48.6823
b | 0.57 |  | 95 | 69.502 | 57.2404 | 49.7291 | 23.75 | 85.5 | 62.5518 | 51.5164 | 44.7562 | 31.6667 | 114 | 83.4025 | 68.6885 | 59.6749 | 39.5833 | 142.5 | 104.2531 | 85.8606 | 74.5937 | b | 0.74 |  | 95 | 87.1797 | 72.9453 | 56.125 | 23.75 | 85.5 | 78.4617 | 65.6507 | 50.5125 | 31.6667 | 114 | 104.6156 | 87.5343 | 67.3499 | 39.5833 | 142.5 | 130.7695 | 109.4179 | 84.1874 | b | 0.64 | 95 | 47.843 | 40.7052 | 33.5976 | 23.75 | 85.5 | 43.0587 | 36.6347 | 30.2378 | 31.6667 | 114 | 57.4116 | 48.8462 | 40.3171 | 39.5833 | 142.5 | 71.7645 | 61.0578 | 50.3964
|  |  | 100 | 71.5641 | 58.9387 | 51.2045 | 25 | 90 | 64.4077 | 53.0448 | 46.0841 | 33.3333 | 120 | 85.8769 | 70.7264 | 61.4454 | 41.6667 | 150 | 107.3461 | 88.408 | 76.8068 |  |  |  | 100 | 90.5523 | 75.7673 | 58.2962 | 25 | 90 | 81.4971 | 68.1905 | 52.4666 | 33.3333 | 120 | 108.6628 | 90.9207 | 69.9555 | 41.6667 | 150 | 135.8285 | 113.6509 | 87.4444 |  |  | 100 | 49.4397 | 42.0636 | 34.7188 | 25 | 90 | 44.4957 | 37.8573 | 31.2469 | 33.3333 | 120 | 59.3276 | 50.4763 | 41.6626 | 41.6667 | 150 | 74.1595 | 63.0954 | 52.0782
|  |  | 105 | 73.5822 | 60.6008 | 52.6485 | 26.25 | 94.5 | 66.224 | 54.5407 | 47.3837 | 35 | 126 | 88.2987 | 72.721 | 63.1782 | 43.75 | 157.5 | 110.3734 | 90.9012 | 78.9728 |  |  |  | 105 | 93.8815 | 78.5528 | 60.4395 | 26.25 | 94.5 | 84.4933 | 70.6975 | 54.3955 | 35 | 126 | 112.6577 | 94.2634 | 72.5274 | 43.75 | 157.5 | 140.8222 | 117.8292 | 90.6592 |  |  | 105 | 51.0078 | 43.3978 | 35.8201 | 26.25 | 94.5 | 45.907 | 39.058 | 32.238 | 35 | 126 | 61.2094 | 52.0774 | 42.9841 | 43.75 | 157.5 | 76.5117 | 65.0967 | 53.7301
|  |  | 110 | 75.5595 | 62.2292 | 54.0633 | 27.5 | 99 | 68.0035 | 56.0063 | 48.6569 | 36.6667 | 132 | 90.6714 | 74.675 | 64.8759 | 45.8333 | 165 | 113.3392 | 93.3438 | 81.0949 |  |  |  | 110 | 97.1696 | 81.3041 | 62.5563 | 27.5 | 99 | 87.4526 | 73.1736 | 56.3007 | 36.6667 | 132 | 116.6035 | 97.5649 | 75.0676 | 45.8333 | 165 | 145.7544 | 121.9561 | 93.8345 |  |  | 110 | 52.5493 | 44.7093 | 36.9025 | 27.5 | 99 | 47.2944 | 40.2384 | 33.2123 | 36.6667 | 132 | 63.0591 | 53.6512 | 44.2831 | 45.8333 | 165 | 78.8239 | 67.064 | 55.3538
|  |  | 115 | 77.4984 | 63.8261 | 55.4506 | 28.75 | 103.5 | 69.7486 | 57.4435 | 49.9055 | 38.3333 | 138 | 92.9981 | 76.5913 | 66.5407 | 47.9167 | 172.5 | 116.2476 | 95.7391 | 83.1759 |  |  |  | 115 | 100.4191 | 84.023 | 64.6483 | 28.75 | 103.5 | 90.3771 | 75.6207 | 58.1835 | 38.3333 | 138 | 120.5029 | 100.8276 | 77.5779 | 47.9167 | 172.5 | 150.6286 | 126.0345 | 96.9724 |  |  | 115 | 54.0657 | 45.9995 | 37.9675 | 28.75 | 103.5 | 48.6592 | 41.3996 | 34.1707 | 38.3333 | 138 | 64.8789 | 55.1994 | 45.561 | 47.9167 | 172.5 | 81.0986 | 68.9993 | 56.9512
|  |  | 120 | 79.4015 | 65.3934 | 56.8122 | 30 | 108 | 71.4613 | 58.854 | 51.131 | 40 | 144 | 95.2817 | 78.472 | 68.1746 | 50 | 180 | 119.1022 | 98.0901 | 85.2183 |  |  |  | 120 | 103.632 | 86.7113 | 66.7167 | 30 | 108 | 93.2688 | 78.0402 | 60.045 | 40 | 144 | 124.3584 | 104.0536 | 80.0601 | 50 | 180 | 155.448 | 130.067 | 100.0751 |  |  | 120 | 55.5586 | 47.2697 | 39.0158 | 30 | 108 | 50.0028 | 42.5427 | 35.1143 | 40 | 144 | 66.6703 | 56.7236 | 46.819 | 50 | 180 | 83.3379 | 70.9045 | 58.5238
|  |  | 125 | 81.2707 | 66.9328 | 58.1496 | 31.25 | 112.5 | 73.1436 | 60.2395 | 52.3347 | 41.6667 | 150 | 97.5248 | 80.3194 | 69.7796 | 52.0833 | 187.5 | 121.906 | 100.3992 | 87.2245 |  |  |  | 125 | 106.8103 | 89.3707 | 68.7629 | 31.25 | 112.5 | 96.1293 | 80.4336 | 61.8866 | 41.6667 | 150 | 128.1724 | 107.2448 | 82.5154 | 52.0833 | 187.5 | 160.2154 | 134.056 | 103.1443 |  |  | 125 | 57.0293 | 48.5209 | 40.0486 | 31.25 | 112.5 | 51.3263 | 43.6688 | 36.0438 | 41.6667 | 150 | 68.4351 | 58.2251 | 48.0583 | 52.0833 | 187.5 | 85.5439 | 72.7814 | 60.0729
|  |  | 130 | 83.108 | 68.446 | 59.4643 | 32.5 | 117 | 74.7972 | 61.6014 | 53.5178 | 43.3333 | 156 | 99.7296 | 82.1352 | 71.3571 | 54.1667 | 195 | 124.662 | 102.669 | 89.1964 |  |  |  | 130 | 109.9557 | 92.0025 | 70.7878 | 32.5 | 117 | 98.9601 | 82.8023 | 63.7091 | 43.3333 | 156 | 131.9469 | 110.403 | 84.9454 | 54.1667 | 195 | 164.9336 | 138.0038 | 106.1818 |  |  | 130 | 58.4789 | 49.7543 | 41.0666 | 32.5 | 117 | 52.631 | 44.7788 | 36.9599 | 43.3333 | 156 | 70.1747 | 59.7051 | 49.2799 | 54.1667 | 195 | 87.7183 | 74.6314 | 61.5999
|  |  | 135 | 84.9152 | 69.9344 | 60.7573 | 33.75 | 121.5 | 76.4237 | 62.9409 | 54.6816 | 45 | 162 | 101.8982 | 83.9212 | 72.9088 | 56.25 | 202.5 | 127.3728 | 104.9016 | 91.136 |  |  |  | 135 | 113.0698 | 94.6082 | 72.7927 | 33.75 | 121.5 | 101.7628 | 85.1473 | 65.5134 | 45 | 162 | 135.6838 | 113.5298 | 87.3512 | 56.25 | 202.5 | 169.6047 | 141.9122 | 109.189 |  |  | 135 | 59.9086 | 50.9707 | 42.0706 | 33.75 | 121.5 | 53.9177 | 45.8736 | 37.8635 | 45 | 162 | 71.8903 | 61.1648 | 50.4847 | 56.25 | 202.5 | 89.8629 | 76.456 | 63.1059
|  |  | 140 | 86.6938 | 71.3992 | 62.0299 | 35 | 126 | 78.0244 | 64.2593 | 55.8269 | 46.6667 | 168 | 104.0326 | 85.679 | 74.4359 | 58.3333 | 210 | 130.0407 | 107.0988 | 93.0449 |  |  |  | 140 | 116.1541 | 97.1888 | 74.7783 | 35 | 126 | 104.5387 | 87.4699 | 67.3004 | 46.6667 | 168 | 139.3849 | 116.6266 | 89.7339 | 58.3333 | 210 | 174.2311 | 145.7832 | 112.1674 |  |  | 140 | 61.3193 | 52.1709 | 43.0613 | 35 | 126 | 55.1874 | 46.9538 | 38.7552 | 46.6667 | 168 | 73.5832 | 62.6051 | 51.6735 | 58.3333 | 210 | 91.979 | 78.2564 | 64.5919
|  |  | 145 | 88.4453 | 72.8417 | 63.2832 | 36.25 | 130.5 | 79.6008 | 65.5575 | 56.9548 | 48.3333 | 174 | 106.1344 | 87.4101 | 75.9398 | 60.4167 | 217.5 | 132.668 | 109.2626 | 94.9247 |  |  |  | 145 | 119.2098 | 99.7456 | 76.7455 | 36.25 | 130.5 | 107.2888 | 89.7711 | 69.0709 | 48.3333 | 174 | 143.0518 | 119.6948 | 92.0946 | 60.4167 | 217.5 | 178.8147 | 149.6185 | 115.1182 |  |  | 145 | 62.712 | 53.3559 | 44.0393 | 36.25 | 130.5 | 56.4408 | 48.0203 | 39.6354 | 48.3333 | 174 | 75.2545 | 64.027 | 52.8472 | 60.4167 | 217.5 | 94.0681 | 80.0338 | 66.059
|  |  | 150 | 90.1711 | 74.263 | 64.5179 | 37.5 | 135 | 81.154 | 66.8367 | 58.0661 | 50 | 180 | 108.2053 | 89.1156 | 77.4215 | 62.5 | 225 | 135.2566 | 111.3945 | 96.7769 |  |  |  | 150 | 122.2383 | 102.2796 | 78.6952 | 37.5 | 135 | 110.0145 | 92.0517 | 70.8257 | 50 | 180 | 146.6859 | 122.7356 | 94.4342 | 62.5 | 225 | 183.3574 | 153.4194 | 118.0428 |  |  | 150 | 64.0876 | 54.5262 | 45.0053 | 37.5 | 135 | 57.6788 | 49.0736 | 40.5048 | 50 | 180 | 76.9051 | 65.4314 | 54.0063 | 62.5 | 225 | 96.1314 | 81.7893 | 67.5079
|  |  | 155 | 91.8722 | 75.664 | 65.7351 | 38.75 | 139.5 | 82.685 | 68.0976 | 59.1616 | 51.6667 | 186 | 110.2467 | 90.7968 | 78.8821 | 64.5833 | 232.5 | 137.8083 | 113.496 | 98.6027 |  |  |  | 155 | 125.2406 | 104.7917 | 80.628 | 38.75 | 139.5 | 112.7165 | 94.3126 | 72.5652 | 51.6667 | 186 | 150.2887 | 125.7501 | 96.7536 | 64.5833 | 232.5 | 187.8609 | 157.1876 | 120.942 |  |  | 155 | 65.4467 | 55.6825 | 45.9597 | 38.75 | 139.5 | 58.902 | 50.1143 | 41.3637 | 51.6667 | 186 | 78.536 | 66.819 | 55.1517 | 64.5833 | 232.5 | 98.17 | 83.5238 | 68.9396
|  |  | 160 | 93.5499 | 77.0458 | 66.9355 | 40 | 144 | 84.195 | 69.3412 | 60.242 | 53.3333 | 192 | 112.2599 | 92.4549 | 80.3226 | 66.6667 | 240 | 140.3249 | 115.5687 | 100.4033 |  |  |  | 160 | 128.2179 | 107.2829 | 82.5447 | 40 | 144 | 115.3961 | 96.5546 | 74.2903 | 53.3333 | 192 | 153.8614 | 128.7395 | 99.0537 | 66.6667 | 240 | 192.3268 | 160.9243 | 123.8171 |  |  | 160 | 66.7901 | 56.8255 | 46.9031 | 40 | 144 | 60.1111 | 51.143 | 42.2128 | 53.3333 | 192 | 80.1481 | 68.1906 | 56.2838 | 66.6667 | 240 | 100.1852 | 85.2383 | 70.3547
|  |  | 165 | 95.2053 | 78.4091 | 68.1199 | 41.25 | 148.5 | 85.6847 | 70.5682 | 61.3079 | 55 | 198 | 114.2463 | 94.0909 | 81.7439 | 68.75 | 247.5 | 142.8079 | 117.6136 | 102.1799 |  |  |  | 165 | 131.171 | 109.7538 | 84.4459 | 41.25 | 148.5 | 118.0539 | 98.7785 | 76.0013 | 55 | 198 | 157.4052 | 131.7046 | 101.3351 | 68.75 | 247.5 | 196.7565 | 164.6308 | 126.6689 |  |  | 165 | 68.1185 | 57.9557 | 47.836 | 41.25 | 148.5 | 61.3067 | 52.1602 | 43.0524 | 55 | 198 | 81.7422 | 69.5469 | 57.4032 | 68.75 | 247.5 | 102.1778 | 86.9336 | 71.754
|  |  | 170 | 96.8392 | 79.7547 | 69.289 | 42.5 | 153 | 87.1552 | 71.7792 | 62.3601 | 56.6667 | 204 | 116.207 | 95.7056 | 83.1468 | 70.8333 | 255 | 145.2587 | 119.6321 | 103.9335 |  |  |  | 170 | 134.101 | 112.2054 | 86.3322 | 42.5 | 153 | 120.6909 | 100.9849 | 77.699 | 56.6667 | 204 | 160.9212 | 134.6465 | 103.5986 | 70.8333 | 255 | 201.1515 | 168.3081 | 129.4983 |  |  | 170 | 69.4325 | 59.0737 | 48.7587 | 42.5 | 153 | 62.4892 | 53.1663 | 43.8829 | 56.6667 | 204 | 83.319 | 70.8884 | 58.5105 | 70.8333 | 255 | 104.1487 | 88.6105 | 73.1381
|  |  | 175 | 98.4525 | 81.0834 | 70.4434 | 43.75 | 157.5 | 88.6073 | 72.9751 | 63.399 | 58.3333 | 210 | 118.143 | 97.3001 | 84.532 | 72.9167 | 262.5 | 147.6788 | 121.6251 | 105.665 |  |  |  | 175 | 137.0086 | 114.6383 | 88.2041 | 43.75 | 157.5 | 123.3078 | 103.1745 | 79.3837 | 58.3333 | 210 | 164.4103 | 137.566 | 105.8449 | 72.9167 | 262.5 | 205.5129 | 171.9575 | 132.3061 |  |  | 175 | 70.7326 | 60.1798 | 49.6717 | 43.75 | 157.5 | 63.6594 | 54.1618 | 44.7046 | 58.3333 | 210 | 84.8792 | 72.2158 | 59.6061 | 72.9167 | 262.5 | 106.0989 | 90.2697 | 74.5076
|  |  | 180 | 100.0462 | 82.3959 | 71.5836 | 45 | 162 | 90.0416 | 74.1563 | 64.4253 | 60 | 216 | 120.0554 | 98.8751 | 85.9003 | 75 | 270 | 150.0693 | 123.5939 | 107.3754 |  |  |  | 180 | 139.8947 | 117.0532 | 90.0621 | 45 | 162 | 125.9053 | 105.3479 | 81.0559 | 60 | 216 | 167.8737 | 140.4638 | 108.0746 | 75 | 270 | 209.8421 | 175.5798 | 135.0932 |  |  | 180 | 72.0195 | 61.2747 | 50.5754 | 45 | 162 | 64.8175 | 55.1472 | 45.5179 | 60 | 216 | 86.4233 | 73.5296 | 60.6905 | 75 | 270 | 108.0292 | 91.912 | 75.8631
|  |  | 185 | 101.6209 | 83.6928 | 72.7104 | 46.25 | 166.5 | 91.4588 | 75.3236 | 65.4393 | 61.6667 | 222 | 121.9451 | 100.4314 | 87.2524 | 77.0833 | 277.5 | 152.4313 | 125.5393 | 109.0655 |  |  |  | 185 | 142.7601 | 119.4507 | 91.9068 | 46.25 | 166.5 | 128.4841 | 107.5056 | 82.7161 | 61.6667 | 222 | 171.3121 | 143.3408 | 110.2882 | 77.0833 | 277.5 | 214.1401 | 179.1761 | 137.8602 |  |  | 185 | 73.2935 | 62.3586 | 51.4701 | 46.25 | 166.5 | 65.9641 | 56.1228 | 46.3231 | 61.6667 | 222 | 87.9522 | 74.8303 | 61.7641 | 77.0833 | 277.5 | 109.9402 | 93.5379 | 77.2051
|  |  | 190 | 103.1774 | 84.9748 | 73.8241 | 47.5 | 171 | 92.8597 | 76.4773 | 66.4417 | 63.3333 | 228 | 123.8129 | 101.9697 | 88.5889 | 79.1667 | 285 | 154.7661 | 127.4621 | 110.7361 |  |  |  | 190 | 145.6054 | 121.8314 | 93.7385 | 47.5 | 171 | 131.0448 | 109.6483 | 84.3647 | 63.3333 | 228 | 174.7264 | 146.1977 | 112.4863 | 79.1667 | 285 | 218.408 | 182.7471 | 140.6078 |  |  | 190 | 74.5552 | 63.4321 | 52.3561 | 47.5 | 171 | 67.0996 | 57.0889 | 47.1205 | 63.3333 | 228 | 89.4662 | 76.1185 | 62.8273 | 79.1667 | 285 | 111.8327 | 95.1481 | 78.5342
|  |  | 195 | 104.7164 | 86.2423 | 74.9252 | 48.75 | 175.5 | 94.2448 | 77.618 | 67.4327 | 65 | 234 | 125.6597 | 103.4907 | 89.9103 | 81.25 | 292.5 | 157.0747 | 129.3634 | 112.3878 |  |  |  | 195 | 148.4312 | 124.1959 | 95.5578 | 48.75 | 175.5 | 133.5881 | 111.7763 | 86.002 | 65 | 234 | 178.1175 | 149.0351 | 114.6694 | 81.25 | 292.5 | 222.6469 | 186.2938 | 143.3367 |  |  | 195 | 75.805 | 64.4954 | 53.2338 | 48.75 | 175.5 | 68.2245 | 58.0459 | 47.9104 | 65 | 234 | 90.9659 | 77.3945 | 63.8805 | 81.25 | 292.5 | 113.7074 | 96.7431 | 79.8507
|  |  | 200 | 106.2386 | 87.4959 | 76.0143 | 50 | 180 | 95.6147 | 78.7463 | 68.4129 | 66.6667 | 240 | 127.4863 | 104.995 | 91.2172 | 83.3333 | 300 | 159.3579 | 131.2438 | 114.0215 |  |  |  | 200 | 151.2383 | 126.5447 | 97.365 | 50 | 180 | 136.1145 | 113.8902 | 87.6285 | 66.6667 | 240 | 181.486 | 151.8536 | 116.838 | 83.3333 | 300 | 226.8575 | 189.817 | 146.0475 |  |  | 200 | 77.0433 | 65.549 | 54.1034 | 50 | 180 | 69.3389 | 58.9941 | 48.693 | 66.6667 | 240 | 92.4519 | 78.6588 | 64.924 | 83.3333 | 300 | 115.5649 | 98.3234 | 81.155
[9 empty] | Approx. Über Origin / q/q110 mittel=f/Vwasser |  | 2000-01-13 | [12 empty] | 735 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[9 empty] | y0 |  | 0.46176 | [12 empty] | 740 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[9 empty] | A1 |  | 0.57752 | [12 empty] | 745 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[9 empty] | t1 |  | 51.9718 | [12 empty] | 750 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[9 empty] | A2 |  | 0.17134 | [12 empty] | 755 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[9 empty] | t2 |  | 581.433 | [12 empty] | 760 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[24 empty] | 765 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!
[24 empty] | 770 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE!

## DP_Wasser_GEA (hidden)
| Vierleiter-Kühlen |  | Vierleiter-heizen |  | Zweileiter - Kühlen |  | Zweileiter- Heizen
| Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT | Wärmeaustauscher | Anschluß - WT
Rohrlänge | 2.312 |  | 2.312 |  | 2.312 |  | 2.312
Anzahl Rohre : | 12 |  | 4 |  | 8 |  | 8
Anzahl Rohrbögen(90°) : | 22 | 2 | 6 | 2 | 14 | 2 | 14 | 2
z-Wert pro Bogen: | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Rohrlänge pro Wasserkreis: | 27.744 | 0.4 | 9.248 | 0.4 | 18.496 | 0.4 | 18.496 | 0.4
sonstige z-Werte : |  | 1.5 |  | 1.5 |  | 1.5 |  | 1.5
z-Wert pro Wasserkreis: | 15.4 | 2.9 | 4.2 | 2.9 | 9.8 | 2.9 | 9.8 | 2.9
Di -Rohr: | 0.0113 | 0.011 | 0.0113 | 0.011 | 0.0113 | 0.011 | 0.0113 | 0.011
Wassertemp. | 60.7634 | 60.7634 | 91.5289 | 91.5289 | 60.6047 | 60.6047 | 92.3255 | 92.3255

## Sprache (hidden)
Ziel-Zelle | DE | GB | NL | Spanisch | Franz | Ital | Danish
B2 | Vierleiter | 2 water circuits | 4-pijps | 4 tubos | 4 tubes | 4 tubi | 4 rørs
D2 | Zweileiter | 1 water circuit | 2-pijps | 2 tubos | 2 tubes | 2 tubi | 2 rørs
A2 | Eingaben DID | Input DID | Gegevens DID | datos DID | données DID | dati DID | Input DID
B3 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
C3 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
D3 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
E3 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
A4 | Vwasser DID | Vwater DID | Waterhoeveelheid DID | V agua DID | V eau DID | Vacqua DID | V vand DID
A5 | Gerätelänge Ln | Unit length | Apparaatlengte | longitud | longueur nominale LN | Lunghezza nominale LN | Effektiv længde
A6 | Düsen Typ | Nozzle-type | Düsen Type | tipo de toberas | type de buse | Tipo di ugello | Dyse størrelse
A7 | Vluftprimär DID | Vair-primary DID | Primaire luchthoeveelheid | V aire primario | débit d'air primaire DID | Portata aria primaria DID | V primær luft
A9 | N-Düsen aktiv | No-nozzles active | Aantal düsen actief | n·toberas activas | buse N active | n° ugelli attivi | Antal aktive dyser
A10 | Eingabe Temperaturen | Input temperatures | Invoer temperaturen | datos temperatura | données températures | Temperature richieste | Temperatur set
A11 | Tluftprimär | Tair-primary | Temp. primairelucht | Temperatura aire primario | température d'air primaire | Temperatura aria primaria | T primær luft ind
A12 | Traum / rel. Luftfeuchte | Troom / rel. Humidity | Temp.ruimte | Temperatura ambiente | température ambiente | Temperatura ambiente | T rum
A13 | Twasser vor | Twater-flow | Temp.water intrede | Temperatura agua impulsion | température d'entrée d'eau | Temperatura acqua di entrata | T vand ind
A18 | Ergebnisse | results | Gegeven | resultados | résultats | risultati | Resultat
A20 | DTwasser | Dtwater | Temp. verschil water | Dt agua | DT température eau (entrée et sortie) | Dt acqua | DT vand
A21 | Twasser rück | Twater-return | Temp. retourwater | Temperatura agua retorno | température de l'eau de retour | Temperatura acqua di ritorno | T vand retur
A22 | DT Raum-vor | DT room - water flow | Temp. verschil ruimte-watertoev. | Dt ambiente agua | DT ambiente eau | Dt ambiente - acqua | DT rum ind
A23 | DT Raum-mittel | DT Room water average | Temp. verschil ruimte-gem.watertemp. | Dt amb.temp.media agua | DT ambiente eau moyenne | Dt ambiente - Tmedia dell'acqua | DT rum middel
A28 | Q wasser DID | Q water DID | Q water DID | Q agua DID | Q eau DID | Q acqua DID | Q vand DID
A29 | Q luft DID | Q air DID | Q lucht DID | Q aire DID | Q air DID | Q aria DID | Q luft DID
A30 | Q DID | Q DID | Q DID | Q DID | Q DID | Q totale DID | Q DID
A31 | DP wasser | DP water | DP water | Dp agua | DP eau | DP acqua | DP vand
A32 | DP luft | DP air | DP lucht | Dp aire | DP air | DP aria | DP luft
A33 | Lwa | NC (incl. 10 dB absorbtion) | Lwa | Lwa | Lwa | Lwa | Lwa
A36 | vL | vL | vL | vL | vL | vL | vL
A37 | vH1 | vH1 | vH1 | vH1 | vH1 | vH1 | vH1
A38 | DTL | DTL | DTL | DTL | DTL | DTL | DTL
A39 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1 | DTH1
A40 | X-krit | X-crit | X-krit | X-krit | x-critique | x-critico | X-kritisk
A41 | Archimedes-Zahl | Archimedes-number | Archimedes-nummer | numero de Arquimedes | nombre d'Archimède | numero di Archimede | Archimedes-tal
A42 | DTzu | DTsupply | DT toevoer | DT impulsion | DT soufflage | Dt mandata | DT ind
F2 | Projekt | Project | Project | Proyecto | Projet | Progetto | Projekt
G2 | Raum-Nr. | room-No. | Ruimte-nr. | local No | numéro du local | Locale nr | Rum nr.
H2 | Bezeichnung | comment | Codering | referencia | désignation | Commento | Betegnelse
A1 | DID 600 Auslegung | DID 600 calculation | DID 600 selectie | calculo DID 600 | sélection DID 600 | Selezione DID 600 | DID 600 dimensionering
B10 | Kühlfall | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køle situation
D10 | Heizfall | heating | Verwarmen | calefacion | chauffage | riscaldamento | Varme situation
F10 | Eingaben Raumgeometrie | Input room measures | Opgave ruimteafmetingen | dimensiones local | dimensions du local | dimensioni del locale | Rum dimensioner
F11 | Raumhöhe | room height | Ruimtehoogte | altura | hauteur du local | altezza del locale | Rumhøjde
B18 | Vierleiter | 2 water circuits | 4-pijps | 4 tubos | 4 tubes | 4 tubi | 4 rørs
B19 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
C19 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
D18 | Zweileiter | 1 water circuit | 2-pijps | 2 tubos | 2 tubes | 2 tubi | 2 rørs
D19 | Kühlen | cooling | Koelen | refrigeracion | rafraîchissement | raffreddamento | Køling
E19 | Heizen | heating | Verwarmen | calefacion | chauffage | riscaldamento | Opvarmning
F36 | Hilfswerte | support values | Hulpwaarden | valores de ayuda | données complémentaires | dati complementari | Hjælpeværdier
F37 | N-Düsen nominell offen | N-active nozzles | N-Düsen standaard geopend | N-toberas activas | buse N active | n° ugelli attivi | N-dyser nominelt åbne
F38 | N-Düsen | N-nozzles total | N-Düsen | N-total de toberas | nombre de buses | numero totale ugelli | Dyse antal
F39 | Aeff | Aeff | Aeff | A efectiva | Aeff | Aeff | Aeff
F40 | veff | veff | veff | v efectiva | veff | veff | veff
F41 | H1 | H1 | H1 | H1 | H1 | H1 | H1
F42 | L | L | L | L | L | L | L
G30 | Sprache | Language | Taal | lenguaje | langue | lingua | Sprog
A14 | Twasser rück | Twater-return | Temp. retourwater | Temperatura agua retorno | température de l'eau de retour | T acqua di ritorno | T vand retur
| Einheit Primärluftvolumenstrom:l/s | Unit primary airflow:l/s | Hoeveelheid primaire lucht: l/s | aire primario en l/s | débit d'air primaire: l/s | portata aria primaria l/s | Enhed primærluft: l/s
| Einheit Primärluftvolumenstrom:m³/h | Unit primary airflow:CFM | Hoeveelheid primaire lucht: m³/h | aire primario en m3/h | débit d'air primaire: m3/h | portata aria primaria m3/h | Enhed primærluft: m3/h
| Standard-Düsenanzahl(aktiv) wiederherstellen | Restore no. of standard active nozzles | Standaard aantal actieve düsen instellen | No.de tob.estand.activas | restauration nombre de buses actives standard | N° fuori standard di ugelli | Retur til standard dyseantal
| 70% - Gitter/Lochblech | 70% - free area | 70% - vrije doorlaat rooster | Reja chap.perforada 70% | 70%-grille/tôle perforée | Lamiera forata al 70% | 70% - frit areal
| 50% - Lochblech | 50% - free area | 50% - vrije doorlaat perforatie | chapa perforada 50% | 50%-tôle perforée | Lamiera forata al 50% | 50% - frit areal
| Details einblenden | details ON | details invoegen | details ON | détails on (afficher les détails) | Dettagli on (scoprire i dettagli) | detaljer on
| Details AUS | details OFF | details wissen | details OFF | détails off (ne plus afficher les détails) | Dettagli off (nascondere i dettagli) | detaljer off
| Vwasser DID = konst | Vwater DID = const | Vwater DID = const | Vwater DID = const | V eau DID=constant | Portata acqua DID=costante | V vand DID = konstant
| DTwasser DID = konst | DTwater DID = const | DTwater DID = const | DTwater DID = const | DT eau DID=constant | Dt acqua DID=costante | DT vand DID = konstant
| DID-Länge Ln ungültig | DID-lenght not valid | DID-lenght not valid | DID-lenght not valid | longueur DID Ln non valide | Lunghezza DID Ln non valida | Ugyldig længde
| muss zwischen 900 und 3000mm liegen | must be 3 to 10 ft | must be 900 to 3000mm | must be 900 to 3000mm | doit être compris entre 900 et 3000 mm | deve essere compreso fra 900 e 3000 | Skal være 900 - 3000 mm
| Warnung: Gerätelänge | Attention: Unit length | Attention: Unit length | Attention: Unit length | attention: longueur de l'appareil | attenzione: lunghezza dell'apparechiatura | Bemærk: aggregatlængde
| Anzahl muss im Bereich von | No Nozzels must be | No Nozzels must be | No Nozzels must be | nombre des buses doit être compirs entre et | N° di ugelli deve essere compreso | Antal dyser skal være
| bis | to | to | to | à | fino a | til
| Warnung: Anzahl aktiver Düsen im nicht zulässigen Bereich | Attention: No of active nozzles not in allowed range | Attention: No of active nozzles not in allowed range | Attention: No of active nozzles not in allowed range | attention: nombre de buses actives non valid | Attenzione: numero di ugelli attivi non valido | Bemærk: Aktivt dyseantal ikke tilladt
| Düsenaustritts-Luftgeschwindigkeit zu gering | Nozzle-velocity too low | Nozzle-velocity too low | Nozzle-velocity too low | débit de sortie des buses trop faible | velocità uscita ugelli troppo bassa | Dysehastighed for lav
| muss größer als 9m/s sein | must be > 1800 FPM | must be > 9m/s | must be > 9m/s | doit être supérieur à 9m/s | deve essere > 9 m/s | Skal være > 9 m/s
| Warnung: Düsen-Luftaustrittsgeschwindigkeit | Attention: nozzle velocity | Attention: nozzle velocity | Attention: nozzle velocity | attention: débit de sortie des buses | Attenzione: velocità uscita ugelli | Bemærk: dysehastighed
| Wasservolumentrom zu hoch. | water-flow rate too high | water-flow rate too high | water-flow rate too high | débit d'eau trop élevé | portata acqua troppo elevata | Vand flow for højt
| Werte müssen unter 250 l/h liegen | must be below 1.5 GPM | must be below 250 l/h | must be below 250 l/h | valeurs doivent être inférieures à 250l/h | Valore deve essere inferiore a 250 l/h | skal være under 250 l/h
| Warnung: Wasservolumenstrom | Attention: water-flow rate | Attention: water-flow rate | Attention: water-flow rate | attention: débit d'eau | Attenzione al livello della portata dell'acqua | Bemærk: Tilladeligt vand flow
| Wasservolumentrom zu niedrig. | water-flow rate too low | water-flow rate too low | water-flow rate too low | débit d'eau trop faible | portata acqua troppo bassa | Vand flow for lavt
| Werte müssen über 30 l/h liegen | must be more than 0.132 GPM | must be more than 30 l/h | must be more than 30 l/h | valeurs doivent être supérieures à 30 l/h | Valore deve essere superiore a 30 l/h | skal være over 30 l/h
| Warnung: Wassertemp. Differenz | Attention: water temp.-difference | Attention: water temp.-difference | Attention: water temp.-difference | attention: différence de température d'eau | attenzione: Dt acqua | Bemærk: vand temp forskel
| Wassertemp.-Differenz unzulässig, | water temp.-difference not valid | water temp.-difference not valid | water temp.-difference not valid | différence de température d'eau non valide | Dt acqua non valido | vand temp forskel ikke tilladt
| muss zwischen 1K und 6K liegen | must be between 3.5 °F and 15.5 °F | must be between 1K and 6K | must be between 1K and 6K | doit être entre 1 K et 6K | deve essere compreso fra 1 K e 6 K | skal være mellem 1K og 6 K
| Wassertemp.-Differenz unzulässig, | Attention: water temp.-difference, | Attention: water temp.-difference, | Attention: water temp.-difference, | différence de température d'eau non valide | Attenzione: Dt acqua | Bemærk: vand temp forskel
| muss zwischen 5K und 30K liegen | must be between 11 °F and 59 °F | must be between 5K and 30K | must be between 5K and 30K | doit être entre 5K et 20K | deve essere compreso fra 5 K e 30 K | skal være mellem 5K og 30K
F30
F28 | Achtung : Taupunktunterschreitung | Attention : passing below the dew point | Attention : passing below the dew point | Attention : passing below the dew point | Attention : passing below the dew point | Attenzione: condizioni al di sotto del punto di rugiada | Attention : passing below the dew point
F43 | Taupunkttemperatur-Kühlfall | room air dew point-cooling | room air dew point-cooling | room air dew point-cooling | room air dew point-cooling | punto di rugiada aria/ambiente | room air dew point-cooling
A43 | Stutzen-Durchmesser / Primärluft | Connection-diameter / primary air | Connection-diameter / primary air | Connection-diameter / primary air | Connection-diameter / primary air | Diametro connessione / aria primaria | Connection-diameter / primary air
| Layout Frontteil | layout room-face | layout rooster | layout perforada | layout perforée | disegno ambiente | Perforering på frontplade

## Katalog_DID600
DID 600 calculation | [10 empty] | Vierleiter-Kühlen | Vierleiter-heizen | Zweileiter-kühlen | Zweileiter-heizen
Input DID | 2 water circuits |  | 1 water circuit |  | Project | room-No. | comment |  |  | 6er düse | 2.9985 | 2.5946 | 5.1844 | 5.1844
| cooling | heating | cooling | heating | [5 empty] | Model: Allometric1 | 0.74 | 0.64 | 0.57 | 0.57
Vwater DID | 0.55 | 0.25 | 0.4845 | 0.4845 | [5 empty] | 8er düse | 2.5089 | 2.2075 | 4.2697 | 4.2697
Unit length | 8 | [8 empty] | Model: Allometric1 | 0.74 | 0.64 | 0.57 | 0.57
Nozzle-type | b | [8 empty] | 10er düse | 1.9304 | 1.8221 | 3.7094 | 3.7094
Vair-primary DID | 80 | [8 empty] | Model: Allometric1 | 0.74 | 0.64 | 0.57 | 0.57
37.7778
No-nozzles active | 72
Input temperatures | cooling |  | heating |  | Input room measures
Tair-primary | 56 |  | 56 |  | room height | 9 |  | Parameter | Wert
Troom / rel. Humidity | 74 | 50 | 70 | 50 | A | 11 |  | ------------------------------------------------------------
Twater-flow | 56 |  | 100 |  | X | 10.5 |  | A | 145.4762 | 86.1905
Twater-return | 64 |  | 84 |  |  |  |  | B1 | -0.41922 | -0.23472
[8 empty] | B2 | 0.00054352 | 0.00033527
[8 empty] | B3 | -3.2253e-07 | -2.0623e-07
[8 empty] | B4 | 9.2593e-11 | 6.0793e-11
results | 2 water circuits |  | 1 water circuit |  |  |  |  | B5 | -1.0288e-14 | -6.8587e-15
| cooling | heating | cooling | heating |  |  |  | B6
Dtwater | -9.5268 | 16.9422 | -9.2094 | 15.349
Twater-return | 65.5268 | 83.0578 | 65.2094 | 84.651
DT room - water flow | -18 | 30 | -18 | 30
DT Room water average | -13.2366 | 21.5289 | -13.3953 | 22.3255
DT-Raum -vor soll | -18 | 30 | -18 | 30
| 0 | 0 | 0 | 0
| 0.58998 | 0.26817 | 0.51972 | 0.51972
| 0.039977 | 0.018171 | 0.035216 | 0.035216 |  |  |  | Parameter | aktiv | Gesamt
Q water DID | -2623.617 | 2120.8012 | -2234.1675 | 3723.6125 | Attention : passing below the dew point |  |  | ------------------------------------------------------------
Q air DID | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | A | 205.5714 | 146.2857
Q DID | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Language |  | B1 | -0.62641 | -0.44191
DP water | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | B2 | 0.00081995 | 0.0006117
DP air | 0.32381 | [6 empty] | B3 | -5.0126e-07 | -3.8496e-07
NC (incl. 10 dB absorbtion) | 23.3723 | [6 empty] | B4 | 1.4871e-10 | 1.1691e-10
Stand : 07.03.2005 | [7 empty] | B5 | -1.7147e-14 | -1.3717e-14
vL | 73.2675 |  | 73.2675 |  | support values
vH1 | 40.2095 |  | 40.2095 |  | N-active nozzles | 64 |  |  | 980 | 146.2857
DTL | #VALUE! |  | #VALUE! |  | N-nozzles total | 74 |  |  | -3.6048 | -0.44191
DTH1 | #VALUE! |  | #VALUE! |  | Aeff | 0.038956 |  |  | 0.00544 | 0.0006117
X-crit | 11.3574 |  | 11.3574 |  | veff | 2053.6081 |  |  | -4.2083e-06 | -3.8496e-07
Archimedes-number | 0.00018299 |  | 0.00018299 |  | H1 | 3.42 |  |  | 1.7747e-09 | 1.1691e-10
DTsupply | #VALUE! | #VALUE! | #VALUE! | #VALUE! | L | 13.92 |  |  | -3.8752e-13 | -1.3717e-14
Connection-diameter / primary air | 4.8425 |  |  |  | room air dew point-cooling | #VALUE! |  |  | 3.4294e-17
Re wasser | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Düsenrohr-D_DP | 100
F wasser | 1.0201 | 0.86146 | 0.99925 | 0.99925 | Düsenrohr-D_LwA | 100
| 42.8576 | 21.3001 | 36.0635 | 36.0635
55.7743
Taupkt °C | #VALUE! | #VALUE!
X g/kg | #VALUE! | #VALUE!
Note on A5: effective lenght Ln
Note on A6: A, B or C
Note on A28: sensible heat
Note on A29: primary air
Note on B4: Flow-rates above 1.500 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on C4: Flow-rates above 1.500 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on D4: Flow-rates above 1.500 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on E4: Flow-rates above 1.500 GPM cause acoustic problems flow-rates below 0.132 GPM cause performance losses
Note on G12: if value is red: check X-krit